## Summary
PROJECT : NATIONAL LAW SCHOOL OF INDIA UNIVERSITY
SUBJECT : Bill of Quantities, SUMMARY
SUMMARY
Sl No | Description | Amount
1 | Supply, installation, testing & commissioning of Grease trap | 0
2 | Supply, installation, testing & commissioning of 300 KLD STP | 0
3 | Supply, installation, testing & commissioning of 200 KLD WTP
4 | Supply, installation, testing & commissioning of Rainwater Harvesting system
5 | Supply, installation, testing & commissioning of External Sewage collection network
6 | Supply, installation, testing & commissioning of Service line
| TOTAL | 0

## Grease trap
PROJECT : NLSIU, Bengaluru
SUBJECT : Bill of Quantities, Grease Trap Installation
Sl.No | DESCRIPTION | UNIT | QTY | RATE (in INR) | AMOUNT (in INR)
0
1 | Supply, installation, testing & commissioning of Oil & Grease Trap with Grease Separator and complete accessories and fittings etc.(for all Buildings where mess/ cafeteria/canteen is available need to be accommodated only for kitchen waste lines)
Make ACO
Location of Oil & grease Trap
| 1. Combined unit for Old & new Annapoorna block | set | 1
| 2. Cafeteria | set | 1
| 3. Boy's Hostel mess | Set | 1
| 4. Cafetria at OAB | Set | 1
| Flow – based on no. of meals | set | 3 |  | 0
2 | Rectification of Plumbing lines to suit the Grease trap connection requirement as per site condition using the Cast Iron Pipes | LS | 1 |  | 0
| T O T A L - PART |  |  |  | 0

## STP
BILL OF QUANTITIES FOR 300 KLD SBR STP WORKS FOR NLSIU, BENGALURU
Sl. No. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
A | SEWAGE TREATMENT PLANT (SBR TECHNOLOGY)
Design, Engineering, Supplying, installing, testing & commissioning of all Equipment/ machinery/ Electrical/ piping for successful operation of Sewage Treatment plant of Below mentioned capacity with results as per state regulatory norms or agreed parameters, cost quoted shall be inclusive of all types of taxes & duties etc. complete all equipment cost should be inclusive of supporting platforms to mount of RCC pedestal and pipe supports required with all metal parts painted with anti-corrosive primer and approved colour of paint
Nature of effluent – 1. Domestic Sewage from toilet, kitchen waste water shall be discharged into the STP. Design to take consideration of same.
Vendor shall submit all necessary backup calculation with data sheets, Vendor shall provide the civil work drawing of Construction, Vendor shall include the any extra item if required.
All pedestals shall be provided with Edge angle protection and painted with Epoxy paint.
Daily average flow – 300 KLD
pH - 6.5 – 8.5
BOD - 260 – 360 Mg/L
S. Solids - 200-300 Mg/L
COD - 400-600 Mg/L
Oil & Grease - Less than 10 Mg / L
Effluent discharge standard after treatment
pH - 6.5 – 8.5
BOD - Less than 10 mg/L
Total Suspended Solids - 20 mg/L
COD - Less than 50 mg/L
Oil & Grease - Less than 10 mg / L
E coli - Nil
Odour - Unobjectionable
Sewage treatment plant shall include the following items:
Manual Bar Screen Chambers
Equalization tank
Anoxic Tank
Aeration Tank
Decant Tank
Disc Filter
Activated Carbon Filter
UV disinfection
Sludge Holding Tank
Air Blowers, Pumps & equipment's
Piping, valves etc
Electrical Panel & Cabling
Final Pumps and related piping
Note:
Contractor shall ensure submission of detailed GA drawings (Plan & Section), P&I diagram, schematic diagram for the above said component and additional component if so required for the complete working of the STP
I | EQUIPMENTS / ELECTRICAL / PIPING
1 | BAR SCREEN UNIT
| Construction of SS 304 Bar screen with 10mm flats x 6mm thick with a 20mm c/c gap with SS 304 scraper with handle, epoxy coated. Size : As required | No. | 1 |  | 0
2 | RAW EFFLUENT TRANSFER PUMP
| Supplying, installing, testing and commissioning of Raw Effluent Transfer pumps (Submersible cutter type). (1W+1S). The Pipe line shall be provided with Bypass connection which shall be connected to nearest sewage pumping line | nos. | 2 |  | 0
Capacity: 33 cum/hr
Make: Grundfos or Equivalent
ALL PUMPS SHALL
Interconnecting piping, fitting, valves within the battery limits of the Sewage Treatment Plant. For Air Lines: MOC of Piping: MS/GI pipe with CI Butterfly Valves For Other Lines: MOC of Piping: UPVC/PVC with CI Butterfly/Ball Valves.
Provision of guide ropes to guide submersible pump from upper level to operational level in sump basin with channels / angle section of MSEP shall be made by the STP contractor.
Contractor is requested to submit quote rate for above pumps Casing & impeller with CI material of construction.
3 | Coarse Bubble Diffusers
| Supplying, installing, testing and commissioning of Coarse Bubble Diffuser with 90mm dia × 800mm long of SS pipe grid with necessary orifices pressure rating with removable deflector to provide clog-free oxygen for equalisation, sludge holding and final collection tank. Of SSI’s Reliable Coarse bubble diffuser Diffuser c/w ¾” MNPT Connection - PCs Make : SSI | No. | 30 |  | 0
Location: Equalization tank, Sludge Holding tank and Final Tank
4 | Fine Bubble Diffusers
Supplying, installing, testing and commissioning of Fine Pore Diffuser with 90mm dia × 1000mm dia long with ss , SS 304 clips PVC support pipe, nylon rope braided hose with all accessories to make it retrievable.-SBR Aeration tank and Anoxic tank
| SSI’s (91X1000mm) length compression moulded EPDM membrane Tube diffuser with 19mm MNPT connection - PCs | No | 32 |  | 0
| Retrievable grid accessories - Sets 1 no. – 1” 3 sides threaded Tee 1no. – ±5m long flexible hose pipe Hooks, clamps and rods for Concrete block. |  |  |  | 0
Make : SSI /Scogen
5 | Blowers
Supplying, installing, testing and commissioning of Roots type air blower Twin lobe roots type Air Blower of adequate capacity of required head comprising of common base frame, suction filter, suction silencer, non return, V belt, safety valve, belt guard, drive and driven pulleys, pressure gauge, inter connection piping, discharge silencer, anti vibration pads including required motor. The entire system has to be provided with acoustic enclosure
| Capacity :-150 m3/ hr @ 0.5 Kg/cm2 (1w +1 stand by Roots Type blower ) for, Equalisation Tank, Sludge Holding Tank and Final tank | Nos. | 2 |  | 0
| Capacity :- 350m3/ hr @ 0.5 Kg/cm2 (1w+1s) Roots type blower for Aeration Tanks | Nos. | 2 |  | 0
Make:Ingresoll Grand/CVT/Everest/ equivalent with acoustics
6 | Decanter valves(automatic)
| Make: Siemens | Nos. | 2
0
7 | Sludge Transfer pumps of required capacity( Horizontal Monoblock pump)
| Capacity:10 cum/hr | Nos. | 4
Make: Grundfos/KBS/Johnson/equivalent
8 | Filter feed pumps of required capacity( Horizontal Monoblock pump) |  |  |  | 0
| Capacity:20 cum/hr | Nos. | 2 |  | 0
Make:Groundfos/KBS/Johnson/equivalent
0
9 | Disc filter | No. | 1
Capacity: 20 cum/hr
Make: Amaid Filters
10 | Activated Carbon Filter(MS Epoxy pressure vessel internally anticorrosive painted, with frontal pipe work, valves etc. Grade of Carbon 500 to 1200 mg/g Iodine value) | No. | 1 |  | 0
MOC:SS
11 | Chlorinator with dosing pump and 100 lts tank |  |  |  | 0
Capacity:0-6LPH
Make:Asia/LMI
12 | Screw Pump to Feed Centrifuge Desludger of required Capacity | set | 1 |  | 0
Capacity:1 cum/hr
Make:Hydroprokav
13 | Sludge Handling system consisting of centrifugal desludger with decanting mechanism suitable for 300 KLD with 3 nos spare bags with required sludge pump of suitable capacity complete with Flocculant dosing system | set | 1 |  | 0
14 | Automatic Ultra Filtration system- Membranes with necessary accessories i.e. auto backwash with CIP tank, instrument & automation. UF system shall be supplied with necessary Dosing systems, UF feed pumps, UF backwash pumps, motors & accessories. | Set | 1
Make: Veolia(Suez)/Torray/equivalent
15 | Disinfection System
| supplying, installing, testing and commissioning of UV Disnfection WWR series. The control panel is mounted in a powder coated mild steel enclosure with universal lock and key. The control panel will have LCD display with indication for power ON, electrode active and electrode worn out. Make : Alfa laval | Nos | 1 |  | 0
16 | Supply, installation, testing and commissioning of front operated, front access, totally enclosed, compartmentalized, free standing, dust and vermin proof Panel with IP 55 ingress protection, fabricated from 3 mm thick CRCA sheets, with hinged, gasketed and lockable doors including the cost of interconnections, copper crimping lugs, brass glands, Rubber mat bonding to earth and painting, suitable for use at 415 volts, 3 phase 4 wire 50 Hz system of suitable capacity at 415 volts complete. The panel must be BMS compatible. Rate shall include necessary feeders of Flushing Pumps and Irrigation Pump. of suitable capacity. Also consider the necessary feeder for ventilation fans. 2 nos | Lot | 1 |  | 0
17 | Supplying, installing, testing and commissioning of Plant Piping, valves, Coupler, MTA, Bush, Ball Valve Plastic, Elbows, Bend, for the system etc complete | Lot | 1 |  | 0
18 | Power / control wiring / Cu. Earth strips /Cable Tray or all the motors and equipment's., the cable shall be of approved make, the tentative cable schedule to be submitted along with tender submission. | Lot | 1 |  | 0
19 | Plant lighting -IP 65 2 X 20W surface LED Lighting fixtures with electronic driver unit with necessary Cabling and conduit accessories. | Lot | 1 |  | 0
20 | Plant Ventilation - As per Tech Spec | Lot
0
21 | Supplying, installing, testing and commissioning of Ultra sonic Flow transmitter in the final tank, equalization tank with 4-20mA output | set | 1 |  | 0
Make : Krohne Marshal / Danfoss / Claire Fontaine / Rockwin
0
22 | Supply, installation, testing and commissioning of Electro Magnetic flow Meter in the inlet of raw sewage pipe with 4-20mA output. The location shall be at header of raw effluent pumps with 3 nos valves for bypass arrangement Make : Krohne Marshal / Danfoss / Claire Fontaine / Rockwin | set | 1 |  | 0
0
23 | Supply, installation, testing and commissioning of Online monitoring system for STP treated water as per CPCB specifications, for measuring pH, BOD, COD, TSS & Outflow | set | 1 |  | 0
0
24 | Supplying, Fixing of Pedestal mounted Eye wash with ABS cover, two high flow water sprays aerated at low pressure which bathe the eyes and face with necessary automatic valve, bowl, spray head assembly which shall be factory assembled. | Set | 1 |  | 0
25 | Full time round the clock and year round, operation of STP including Bar screen, Raw Effluent pumps, Coarse bubble diffusers, Fine Pore Diffuser, Air Blower, Sludge pumps, LT Panel with energy meter, Power wiring, plant lighting and all other items which the successful tenderer as executed in the premises including keeping log books and records if electrical consumption to various areas. | LS | 1
| SUB TOTAL-1 |  |  |  | 0
II | FINAL TREATED WATER PUMPS
#VALUE! |  | Set | 1
1 | Supply, fixing, testing and commissioning of EFF-1 type, Hydro-pneumatic system of Hydro MPC with continuous demand, flow meter and Energy meter. The system shall comprises of 2 nos (1 working & 1 standby) & Pre-charged pressure tank of adequate capacity, pressure switch etc., complete with electric motor at 415V 3Ph 50 Hz required duty conditions mounted on common base plate and wiring from panel to the motor including air volume controls, etc., complete. The quoted rate should also include the required size cabling from panel. | Set | 1 |  | 0
0
| Flow – |  |  |  | 0
| Head – |  |  |  | 0
| no of pump - 1 working + 1 standby (1 SET) |  |  |  | 0
2 | Supplying, installing, fixing, jointing, testing and commissioning of approved make Unplastized Polyvinyl Chloride pipes (uPVC) up to 50mm dia SDR.11, ASTM CTS, and above 50mm dia UPVC schedule 40 ASTM IPS. Fittings up to 50mm dia SDR.11, ASTM CTS and above 50mm dia schedule 40 fittings. The fittings and specials such as tees, elbows, couplers, bends, enlargers etc. with CPVC brass threaded combination / transition specials such as male adapters brass threaded female adapters, brass FPT Tee, Brass FPT elbow etc., where connection with metal is to be made including necessary drilling holes, chasing walls and making the same good in cement mortar 1:1 and restore the same in original condition neatly as directed by the Engineer In-charge. Joints to be made with UPVC solvent cement up to 50mm dia as per ASTM D-2846 and above 50mm dia primer P-70, and solvent conforming to ASTM F-4931 / 724. The solvent used shall be of approved make as recommended by the pipe manufacturer. Rate shall include necessary MS supports, clamps, hanging rods, Grip bolts t etc., complete in all respect. The rate shall include the cost of galvanized U clamps, bolts & nuts,supports with 2 coats of zinc chromate primer with 2 coats of enamel paint of total DFT minimum 100 micron
| a) 65 mm dia (I.D) | Lot
| b) 50 mm dia (I.D) | Lot
| c) 80 mm dia (I.D) | Lot |  |  | 0
| d) 100 mm dia (I.D) | Lot |  |  | 0
3 | Supplying, fixing, testing and commissioning of PVC Soil, waste and ventilating pipes (SWR) conforming to IS:13592 Type B with rubber ring, yellow seal (conforming to IS : 5382) joints inclusive of all necessary specials like bends, tee, offsets, door bends, junctions, cowls, threaded type cleanout etc., laid under floor / fixed on walls and in pipe shaft with proper pipe support like brackets, hangers, G.I grip bolts etc., complete. The support shall be painted with two coats of enamel paint. The rate shall include the cost of galvanized U clamps, bolts & nuts,painting of supports with 2 coats of zinc chromate primer with 2 coats of enamel paint of total DFT minimum 100 micron.
| a) 75 mm dia | Lot |  |  | 0
| b) 110 mm dia | Lot |  |  | 0
| c) 160 mm dia | Lot |  |  | 0
| SUB TOTAL- 2 |  |  |  | 0
III | CIVIL
1 | SURVEYING WORKS |  |  |  | 0
| Survey Total Station with surveyor | Days
0
Centreline marking
| Plot survey after excavation |  |  |  | 0
Floor finish RL marking
| Survey Auto level with surveyor | Days |  |  | 0
2 | EXCAVATION WORKS
Excavation by pneumatic / hydraulic machinery (without blasting)with necessary tools and tackles, in all types of soil for footings / trenches below ground level at all levels and carting away the excavated material within premises / Plot area and depositing/ stacking and or spreading as directed with in the site / campus including all operational incidental labour charges , Including dressing of sides and ramming of bottoms, preparing the bed for the foundation, Including shoring, strutting etc. complete for finished item of work etc complete as directed by the Engineer-In-charge.
And in case of disposing outside Campus then Royalty, expenses to be paid extra with Service charges. And Vendor should indemnify owner against any sort of legal complications on account of outside dumping.
| Soft soil / Murum | Cum |  |  | 0
| Weathered / Soft Rock | Cum |  |  | 0
| Hard Rock | Cum |  |  | 0
| STP | Cum |  |  | 0
3 | BACK FILLING WORKS
i | Filling with approved material brought from surplus excavated material, filling in layers of 20-30 cm.breaking clods, watering and consolidation using Pneumatic Rollers / Plate Compacters and levelling, etc., complete. The proctor density of such compacted fill shall be 95% of standard proctor. The rate to include loading, unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete. And as directed by the Engineer-In-charge.
ii | Supply of approved granular murum material brought from outside of the site including filling in layers of 20-30 cm.matic Rollers / Plate Compacters, watering, compaction with 8 - 10 MT roller levelling etc., complete. The proctor density of such compacted fill shall be 95% of standard proctor. Scope also includes royalty and handling charges from outside etc complete and as directed by the Engineer-In-charge. |  |  |  | 0
| STP | Cum |  |  | 0
4 | PLUM CONCRETE
| Supplying and providing plum concrete of proportion 60% M20 Concrete & 40% Rubble stone for 600 mm to 450 mm thick at required level difference areas in order to maintai the required level including shuttering, concreting, compacting, curing etc complete to all lead and lift etc complete and as directed by the Engineer-In-charge. |  |  |  | 0
| STP | Cum |  |  | 0
5 | PCC WORKS
| Providing and laying in situ Plain Cement Concrete 1:4:8 for foundation, floor bedding etc., including dewatering, formwork, compacting and curing complete at all height/depths. Rate shall include concrete brought from RMC plant or batching plant installed on site or outside site premises by contractor. Concrete Grade M15 etc complete and as directed by the Engineer-In-charge. |  |  |  | 0
| STP | Cum |  |  | 0
6 | REINFORCEMENT WORKS
Supplying, Collecting, fabricating & fixing in position reinforcement for RCC work with high yield strength ribbed cold twisted tor steel (HYSD) bar of various diameters and grade of steel FE 550 at all levels, conforming to IS specification including transporting from yard, decoiling, straightening, cutting, bending, hoisting, fabricating, and placing in position according to drawings and binding the reinforcement with GI annealed binding wire of double fold of 18 gauge and providing PVC cover blocks, for placing the reinforcements in position and for maintaining the cover specified and/or according to relevant IS including dewatering wherever necessary. The rate shall include cost of binding wire, chairs, spacers which will not be measured separately for payment etc complete all as per design, specifications and drawings, with all lead & lift for all materials & labour at all heights & locations. etc complete and as directed, by the Engineer-In-charge.
Quantity of steel as per drawing and with authorised overlaps only shall be measured and paid for. Contractor shall prepare bar bending schedule and fabrication shall be carried out as per bar bending schedules. (Note: All testing ( including physical & chemical) and quality assurances shall be as per the tender conditions/ Specifications and no extra shall be paid for the same.)
| STP walls/Pedestals/supports/miscellaneous concrete items, etc., | MT |  |  | 0
7 | RCC WORKS
Supplying, mixing and placing in position at all levels consolidated and cured as specified controlled grade cement concrete M-30 including, compaction, etc., complete all as directed by the Engineer-In-charge. Design mix to be got approved by the consultant before execution. Very old / non suitable centring materials for formwork decided by the Engineer -In-charge will not be allowed.
The rates quoted shall hold good for all foundations at any depth, flooring, all floors, heights, levels, elevation, below ground level, basement, trenches, pits, tunnels etc. complete.
The charges for Cube tests of concrete at site or Third Party Testing ( from external Agencies ) as per IS standards will be borne by the contractor
| Note: Reinforcement shall be paid separately |  |  |  | 0
| STP |  |  |  | 0
8 | FORM WORK
Providing Centring / Shuttering at all levels for the following works including strutting, propping, bracing, staging, decluttering, cleaning the materials before erection, using approved SYSTEM FORMWORK and shifting the materials from yard to place of work, multiple handling of the materials necessary consumables such as nails, etc complete. Cost to include sealing the joints with heavy duty brown adhesive tape, applying mould releasing agents aligning to line and levels including MS ties, concrete/ PVC cover blocks etc., complete as directed by the Engineer-In-charge. 1. All formwork, moulds, centring and shuttering shall be good quality plastic coated marine plywood/ aluminium sheet/PVC board etc. Rate to include props, nails, spans, etc. 2. Mould releasing agents of approved make shall be used. 3. Item of works shall be either straight, curved, sloped, plain, tapered or circular in shape .
Cost to include supporting system, bracings, platforms required for various elements at various heights and levels . Minimum of 150mm high MS frame works is required for kickers and starters.
Formwork shall be designed for close jointed rigid, durable and shall have adequate strength, water tightness and ensure easy removal etc., Props, shorings and bracings shall be all in steel or Aluminium. Formwork designed with proposed materials (to be approved prior to making) shall be able to retain its shape, line, dimension, level within the allowable limits of variations. Necessary arrangement shall be envisaged to provide camber as per design.
All necessary treatment to honey combed areas, uneven concrete surfaces shall be made proper as per the consultant requirement without any extra cost
| STP | Sqm |  |  | 0
9 | PLASTERING WORKS
a | Internal cement plaster 12 to 15 mm thick - Cement mortar (1:6) plastering 15mm thick for concrete surfaces, finished smooth with trowel including neeru rendering for interior faces of walls including scaffolding, hacking, chicken mesh, curing etc., all complete as directed by the Engineer-In-charge. |  |  |  | 0
| STP | Sqm |  |  | 0
b | External sand faced plaster - Cement mortar (1:6) plastering 20mm thick for brick/concrete surfaces, fair sponge finish for exterior surfaces of walls including scaffolding, hacking, chicken mesh, curing etc., all complete as directed by the Engineer-In-charge |  |  |  | 0
Note: 10% higher side quantity
| STP | Sqm |  |  | 0
10 | PAINTING WORKS
a | OBD - Providing and painting two coats of oil bound washable distemper of Asian make or approved manufacture conforming to I.S.428 with and over a coat of alkali resistant primer including preparation of surface to internal walls and ceiling with all required scaffolding, etc., all complete as directed by the Engineer-In-charge. | Sqm |  |  | 0
b | Apex Ultima Paint for external walls - Providing and painting two coats of EXTERIOR APEX paint of approved colour and manufacture conforming to I.S.5410 over a coat of primer, preparation of surface for external surface of walls and ceiling with all required scaffolding, washing down the surface with water before painting and curing for two days after application of final coat, etc., all complete as directed by the Engineer-In-charge. | Sqm |  |  | 0
11 | DEWATERING
Hire charges for Dewatering pump up to 3HP or as required while excavation and concreting with Operator. Rate to be considered per pump per day for Electrical operated pump.
Repair and Maintenance will be Contractor's scope
Curing Pump should not be considered.
| And in case of Diesel operated pump then Fuel expenses will be reimbursed with Service Charges by Embassy on producing Log sheets, consumption details and certification. | Days |  |  | 0
12 | STP WATER PROOFING WORKS
i | The system consists one coat of primer (master seal P770 or equivalent) approximately 0.3kg/m2 and spray/roller applied membrane system (master seal M790 or equivalent) with 1.0-1.2 kg/m2 to build a thick coating that protects concrete & metal from wide range of chemicals at min 0.7-0.8mm thick coats. After base preparation of cleaning, brushing and removal of flacky materials, grouting the porous area with non-shrink fibre reinforced thixotropic repair mortar / grout. Fixing of weep holes, Grouting of pipe outlets etc with putty / bedding mortar & adhesives and application of system. The coatings shall be applied at intervals and as per the manufacturers specifications. Cost to include the treatment along junctions, corners by making a wata and protecting the same coating both on floor and walls. Cost including grouting all pipe sleeves, cutouts, openings and checked for water tightness with waterproofing admixtures as per manufacturers specifications and consultants approval, curing etc. complete. The product shall comply with the minimum requirements as per ASTM D 4541, D 4060, D 4587-91, C881, Type III, grade 2, clause C with necessary safety precautions. System having crack bridging capacity of up to 0.7mm, max moisture tolerance
Surface method treatment as specified above
0.8-0.9 mm
| Floors | Sqm |  |  | 0
| Walls | Sqm |  |  | 0
ii | Fibre screed concrete with slope for protection of built up membrane systems
Providing, batching, mixing, transporting through transit mixers, pumping and laying controlled Screed Concrete of M20 grade at all levels and heights specified below using ordinary Portland cement of grade 53 from approved manufacturer, sand, 12mm and down size coarse aggregates, necessary admixtures approved by Consultants including all leads and lifts, pumping using line pump or boom placer, vibrating/ compaction, scaffolding wherever necessary, curing as directed at all heights and depths as instructed. Cost to include providing & mixing Graded fibrillated 100% virgin poly propylene fibres in concrete at the rate of 0.90 kg/cum as per manufacturers specifications, to smooth finish and impression marking 300 x 300 Square with 3 mm rod /thread-markings. Treatment to continue along the vertical surface for 300mm height in shape of round water, curing etc. The concrete shall be laid in panels of not more than 200sqm and the joints shall be treated with elastomeric sealants. M20 grade with broom finish at the top for medium traffic density with a minimum thickness of 50mm at drain points and a slope of 1:150. Cost to include necessary bonding agent / primer to be applied on RCC slab, cleaning and preparation of base slab, grouting of all outlets etc. complete.
Screed has to be smooth finish to take any type of Finish (i.e. landscape, wooden flooring etc.) on the surface.
Screed to be laid in panels of not more than 200sqm and the joints shall be treated with Elastomeric Sealants. Expansion joint and Construction joint treatment to be ensured in the Screed panels. Same has to be thread- marked.
Vertical Surface to be 15 mm plastered up to 300 mm ht.
| 110 mm average thickness sloped screed | Sqm |  |  | 0
iii | Protection coating for exposed wall surface by pitch extended Epoxy coating system
The system consists two coats of pitch extended epoxy resin system to build a thick coating that protects concrete & metal from wide range of chemicals at min 300 microns in two coats. After base preparation of cleaning, brushing and removal of flacky materials, grouting the porous area with non-shrink fibre reinforced thixotropic repair mortar / grout. Fixing of weep holes, Grouting of pipe outlets etc with epoxy putty / epoxy bedding mortar & adhesives and application of first coat of resin system and second layer of coating using the same coating when the first coating is still green. The coatings shall be applied at intervals and as per the manufacturers specifications. Cost to include the treatment along junctions, corners by making a wata and protecting the same coating both on floor and walls, curing etc. complete. The product shall comply with the minimum requirements as per ASTM D 4541, D 4060, D 4587-91, C881, Type III, grade 2, clause C with necessary safety precautions.
300 micron
| Wall above platform slab & Ceiling if any | Sqm |  |  | 0
iv | Crystalline Hydrophilic waterproofing coating system
Providing and Applying a waterproof, efflorescence -free, levelling and protective weather resistant render layer of Min 3mm thick, comprising of cements, quartz with graded size distribution and special additives, to be manually applied by trowel or can also be applied by spray application for speedier completion of the work for larger areas. The product/system must be UV resistant, non toxic, Environment friendly, white in colour, have a high impact resistance, with a maximum aggregate size of 0.4mm . The Product/system shall be applied in 2 or 3 coats as required , with a min total consumption of 6 kg/m2 to achieve a total thickness of Min 3mm., all as per manufacturers recommendations , etc complete. The product conforms to Min compressive strength > 30 Mpa at 28 days ageing, Adhesion to concrete surfaces shall be min 2 N/mm2 as per EN 1504-3, and Reaction to fire as per EN 13501-1( Euro class) conforming to A1.
| STP External wall | Sqm |  |  | 0

## WTP
BILL OF QUANTITIES FOR 200 KLD WTP WORKS FOR NLSIU, BENGALURU
Sl. No. | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
A | WATER TREATMENT PLANT
1 | Supplying, Installing, testing and commissioning approved make Screen filter with necessary accessories
a) | Max flow rate = 20 cum/hr,at 10 hrs cycle, Filtration size : 70 microns | unit | 1
2 | Supplying, Installing, testing and commissioning approved make Screen filter with necessary accessories
a) | Max flow rate = 5 cum/hr,at 10 hrs cycle, Filtration size : 70 microns | unit | 1
3 | Supplying, installing, testing and commissioning approved make Activated carbon Filter in MS vessel construction with internals, electrical control system complete with Frontal piping, valves, suitable supports for mounting, pressure gauge, orifice plate etc.., complete as per the detailed specification for the efficient working of system. The maximum working Resin type: 220 Na OBR:150 -180 KL MOC:MS Rubber lined Max. working pressure = 3.5kg/sqcm | unit | 1
4 | Supplying, installing, testing and commissioning of approved make Softener, MS vessel construction. with inlet water quality of approximately 100ppm hardness, & outlet water quality of less than 50 ppm hardness, with electrical control system, & diaphragm valves, 1 flow meters and all other accessories, regeneration tank etc. Resin type: 220 Na OBR:150 -180 KL MOC:MS Rubber lined | unit | 1
5 | supplying, installing, testing and commissioning of UV Disinfection for BWSSB water. The control panel will have LCD display with indication for power ON, electrode active and electrode worn out. Make : Alfa Laval
a) | Duty =5.0 lph | unit | 1
6 | supplying, installing, testing and commissioning of UV Disinfection. The control panel will have LCD display with indication for power ON, electrode active and electrode worn out. Make : Alfa Laval
a) | Duty =15.0 Cum/hr | unit | 1
7 | Supplying, installing, testing and commissioning of inflow meter to Borewell water & outflow meter from WTP inter unit with accessories. | Nos. | 2
Make: Krohne Marshal / Danfoss / Claire Fontaine / Rockwin/Aster
8 | Supplying, installing, testing and commissioning of Raw Water Feed Pumps Supply of Centrifugal Pump Flow rate :- 20 m3/hr, Make :- Kirloskar/ Lubi/ EQV Qty 2 No’s (1working + 1standby) | Nos. | 2
9 | Supplying, installing, testing and commissioning inter unit. UPVC SH 80 piping with necessary flanges, bolts, nuts, neoprene gaskets, with necessary control valves, non return valves etc ., complete. | Lot | 1
| Sub Total -1 |  |  |  | 0
1 | SURVEYING WORKS
| Survey Total Station with surveyor | Days
Centreline marking
Plot survey after excavation
Floor finish RL marking
| Survey Auto level with surveyor | Days
2 | EXCAVATION WORKS
Excavation by pneumatic / hydraulic machinery (without blasting)with necessary tools and tackles, in all types of soil for footings / trenches below ground level at all levels and carting away the excavated material within premises / Plot area and depositing/ stacking and or spreading as directed with in the site / campus including all operational incidental labour charges , Including dressing of sides and ramming of bottoms, preparing the bed for the foundation, Including shoring, strutting etc. complete for finished item of work etc complete as directed by the Engineer-In-charge.
And in case of disposing outside Campus then Royalty, expenses to be paid extra with Service charges. And Vendor should indemnify owner against any sort of legal complications on account of outside dumping.
| Soft soil / Murum | Cum
| Weathered / Soft Rock | Cum
| Hard Rock | Cum
| WTP | Cum
3 | BACK FILLING WORKS
i | Filling with approved material brought from surplus excavated material, filling in layers of 20-30 cm.breaking clods, watering and consolidation using Pneumatic Rollers / Plate Compacters and levelling, etc., complete. The proctor density of such compacted fill shall be 95% of standard proctor. The rate to include loading, unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete. And as directed by the Engineer-In-charge.
WTP
ii | Supply of approved granular murum material brought from outside of the site including filling in layers of 20-30 cm.matic Rollers / Plate Compacters, watering, compaction with 8 - 10 MT roller levelling etc., complete. The proctor density of such compacted fill shall be 95% of standard proctor. Scope also includes royalty and handling charges from outside etc complete and as directed by the Engineer-In-charge.
| WTP | Cum
4 | PLUM CONCRETE
Supplying and providing plum concrete of proportion 60% M20 Concrete & 40% Rubble stone for 600 mm to 450 mm thick at required level difference areas in order to maintain the required level including shuttering, concreting, compacting, curing etc complete to all lead and lift etc complete and as directed by the Engineer-In-charge.
| WTP | Cum
5 | PCC WORKS
Providing and laying in situ Plain Cement Concrete 1:4:8 for foundation, floor bedding etc., including dewatering, formwork, compacting and curing complete at all height/depths. Rate shall include concrete brought from RMC plant or batching plant installed on site or outside site premises by contractor. Concrete Grade M15 etc complete and as directed by the Engineer-In-charge.
| WTP | Cum
6 | REINFORCEMENT WORKS
Supplying, Collecting, fabricating & fixing in position reinforcement for RCC work with high yield strength ribbed cold twisted tor steel (HYSD) bar of various diameters and grade of steel FE 550 at all levels, conforming to IS specification including transporting from yard, decoiling, straightening, cutting, bending, hoisting, fabricating, and placing in position according to drawings and binding the reinforcement with GI annealed binding wire of double fold of 18 gauge and providing PVC cover blocks, for placing the reinforcements in position and for maintaining the cover specified and/or according to relevant IS including dewatering wherever necessary. The rate shall include cost of binding wire, chairs, spacers which will not be measured separately for payment etc complete all as per design, specifications and drawings, with all lead & lift for all materials & labour at all heights & locations. etc complete and as directed, by the Engineer-In-charge.
Quantity of steel as per drawing and with authorised overlaps only shall be measured and paid for. Contractor shall prepare bar bending schedule and fabrication shall be carried out as per bar bending schedules. (Note: All testing ( including physical & chemical) and quality assurances shall be as per the tender conditions/ Specifications and no extra shall be paid for the same.)
| WTP | MT
7 | RCC WORKS
Supplying, mixing and placing in position at all levels consolidated and cured as specified controlled grade cement concrete M-30 including, compaction, etc., complete all as directed by the Engineer-In-charge. Design mix to be got approved by the consultant before execution. Very old / non suitable centring materials for formwork decided by the Engineer -In-charge will not be allowed.
The rates quoted shall hold good for all foundations at any depth, flooring, all floors, heights, levels, elevation, below ground level, basement, trenches, pits, tunnels etc. complete.
The charges for Cube tests of concrete at site or Third Party Testing ( from external Agencies ) as per IS standards will be borne by the contractor
Note: Reinforcement shall be paid separately
WTP
8 | FORM WORK
Providing Centring / Shuttering at all levels for the following works including strutting, propping, bracing, staging, deshuttering, cleaning the materials before erection, using approved SYSTEM FORMWORK and shifting the materials from yard to place of work, multiple handling of the materials necessary consumables such as nails, etc complete. Cost to include sealing the joints with heavy duty brown adhesive tape, applying mould releasing agents aligning to line and levels including MS ties, concrete/ PVC cover blocks etc., complete as directed by the Engineer-In-charge. 1. All formwork, moulds, centring and shuttering shall be good quality plastic coated marine plywood/ aluminium sheet/PVC board etc. Rate to include props, nails, spans, etc. 2. Mould releasing agents of approved make shall be used. 3. Item of works shall be either straight, curved, sloped, plain, tapered or circular in shape .
Cost to include supporting system, bracings, platforms required for various elements at various heights and levels . Minimum of 150mm high MS frame works is required for kickers and starters.
Formwork shall be designed for close jointed rigid, durable and shall have adequate strength, water tightness and ensure easy removal etc., Props, shoring and bracings shall be all in steel or Aluminium. Formwork designed with proposed materials (to be approved prior to making) shall be able to retain its shape, line, dimension, level within the allowable limits of variations. Necessary arrangement shall be envisaged to provide camber as per design.
All necessary treatment to honey combed areas, uneven concrete surfaces shall be made proper as per the consultant requirement without any extra cost
| WTP | Sqm
9 | PLASTERING WORKS
a | Internal cement plaster 12 to 15 mm thick - Cement mortar (1:6) plastering 15mm thick for concrete surfaces, finished smooth with trowel including neeru rendering for interior faces of walls including scaffolding, hacking, chicken mesh, curing etc., all complete as directed by the Engineer-In-charge.
| WTP | Sqm
b | External sand faced plaster - Cement mortar (1:6) plastering 20mm thick for brick/concrete surfaces, fair sponge finish for exterior surfaces of walls including scaffolding, hacking, chicken mesh, curing etc., all complete as directed by the Engineer-In-charge
Note: 10% higher side quantity
| WTP | Sqm
10 | PAINTING WORKS
a | OBD - Providing and painting two coats of oil bound washable distemper of Asian make or approved manufacture conforming to I.S.428 with and over a coat of alkali resistant primer including preparation of surface to internal walls and ceiling with all required scaffolding, etc., all complete as directed by the Engineer-In-charge. | Sqm
b | Apex Ultima Paint for external walls - Providing and painting two coats of EXTERIOR APEX paint of approved colour and manufacture conforming to I.S.5410 over a coat of primer, preparation of surface for external surface of walls and ceiling with all required scaffolding, washing down the surface with water before painting and curing for two days after application of final coat, etc., all complete as directed by the Engineer-In-charge. | Sqm
11 | DEWATERING
Hire charges for Dewatering pump up to 3HP or as required while excavation and concreting with Operator. Rate to be considered per pump per day for Electrical operated pump.
Repair and Maintenance will be Contractor's scope
Curing Pump should not be considered.
| And in case of Diesel operated pump then Fuel expenses will be reimbursed with Service Charges by Embassy on producing Log sheets, consumption details and certification. | Days
12 | WATER PROOFING for WTP
12.1 | BOREPACKING : Preparing the inside surface of core and PVC by roughening using suitable file /sand paper to get better adhesion prior to packing works. Cleaning the surface by wire brushing followed water jet to remove any laitance or loose flaky particles. Providing necessary formwork for packing the bore using suitable arrangement (depending upon site conditions). Applying a coat of styrene- butadiene based polymer coating using SBR LATEX or equivalent makes to enhance adhesion between the packing material and other surfaces Packing the gap using non-shrink cement polymer based grout using NS GROUT up to the surface of the bore whilst the EUCO SBR LATEX is in tacky state. Compressive Strength for 28D :59Mpa (ASTM C109 Modified*) , completely as per the manufacturer’s Instruction. Make Tremco or Equivalent
i | up to 75 mm Dia
ii | 110 mm Día | Sqm
iii | 150-200 mm Dia | Sqm
12.2 | Construction Joint Treatment & Grouting : Chase opening the Construction Joints /Crack by providing “ V ” groove, removing the dust and clean the designated area following by providing chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture GROUT ADMIX-IN @ 250 gms/ bag of cement in the required consistency through the pre fixed PVC nozzles in the 18 mm dia holes, fixing of PVC nozzles with EUCO SPEED PLUG non shrink rapid setting hydraulic cement compound and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is completed using EUCO SPEED PLUG, finishing, curing etc. as per manufacturers specification and as directed. Make Tremco or Equivalent
7.3 | Coving at Right Angles : Providing and Applying angle fillets of size 50mm x 50mm at the junction of slab and vertical offsets with Cement Mortar 1:4 and admixed with EUCO SBR LATEX of make TREMCO CPG India. a carboxylated styrene butadiene copolymer latex admixture @ 200ml/Bag of cement (Cement & Sand shall be supplied free of cost at the point of execution).Make Tremco or Equivalent
Option -1 | Waterproofing layer
Surface Preparation: The substrate to be treated must be sound and even, open pored, roughened and its surface free from voids, large cracks, or ridges. Any adhesion reducing substances like bitumen, oil, grease, remains of paint or laitance must be removed by suitable means. Waterproofing system : providing mixing and applying cementitious, ready-mixed surface waterproofed. a mixing ratio of Vandex BB 75 Powder 6 : water 1 Ltr, A maximum of 3 mm (approx. 6 kg/m²) .Allow to cure for as damping for 5 day by keeping the substrate damp condition. Compressive strength 28 d approx. 40 [MPa]
Bending tensile strength 28 d approx. 6 [MPa]
Static modulus of elasticity 28 d approx. 28 [GPa]
| Capillary absorption : 0.06 [kg/m²·h 0.5] following strictly the instruction as per manufacture and complete as per the vendors methodology approved by consultants/clients ,application work shall be executed by our authorised applicator. Make Tremco or Equivalent | Sqm
Option -2 | Waterproofing layer
12.4 | Surface Preparation: The cleaning and preparation of the substrate to which waterproofing barrier is applied must be carried out thoroughly to leave a sound base for the application. Any laitance present on the surface must be removed mechanically. Release oil and other contaminants which may impair adhesion must be removed prior to the application. Surface shall be maintained in SSD condition / water priming, before applying waterproof coating.
Waterproofing System: Providing mixing and applying high performance two component cement-based, polymer-modified elastomeric coating designed to waterproof concrete and masonry with inherent crack-bridging ability, applied in 2 coats @ 1 Kg/Sqm/Coat. The cured coating, after immersion, It shall have the capability to resist a positive water pressure of 7 bar and a negative water pressure of 3 bar when tested to water pressure (DIN 1048) Dynamic crack1 accommodation: >1.2mm,The product shall comply with the minimum requirements as follows: elongation at break 120% Tensile strength >1.5N/mm2 (ASTM D412), solid content (ASTM C836), water impermeability(DIN 1048), abrasion resistance (ASTM D4060), Adhesion strength (ASTM D4541), following strictly the instruction as per manufacture and complete as per the vendors methodology approved by consultants/clients ,application work shall be executed by our authorised applicator. Make Tremco or Equivalent
12.5 | Protection Layer( Vertical) : Rendering plastering 15mm thick with CM 1:4 by admixing with integral waterproofing compound at the dosage of minimum 150ml/bag of cement over waterproofing layer as per site requirement.
12.6 | Protective layer(Horizontal) : Laying M20 grade screed concrete to required slope admix with integral waterproofing compound at the dosage of minimum 150ml/bag of cement, Incorporate a micro synthetic fibre PSI FIBERSTRANDS F at a dosage of 0.9kg .Cum .lay over waterproofing layer to a minimum thickness of 75mm as per site requirement. | Sqm
12.7 | Food Grade Epoxy Coating : supplying and applying water-based food grade epoxy resin system shall be applied in two coats of water-based epoxy resin at 0.5 kg/sq. m( @ 0.25Kg/Sqm/coat) over the plastered /screed surface .having Vapour Permeability as per ASTM: E96:90-20g/ m2/mm /24 hr and Bond Strength Greater than cohesive strength of substrate. >1.5 MPa, adhesion strength ASTM D 4541. Complete as per manufacturer recommendation etc. Application work shall be executed by our authorised applicator. Make Tremco or Equivalent
iv | Crystalline Hydrophilic waterproofing coating system
12.8 | Providing and Applying a waterproof, efflorescence -free, levelling and protective weather resistant render layer of Min 3mm thick, comprising of cements, quartz with graded size distribution and special additives, to be manually applied by trowel or can also be applied by spray application for speedier completion of the work for larger areas. The product/system must be UV resistant, non toxic, Environment friendly, white in colour, have a high impact resistance, with a maximum aggregate size of 0.4mm . The Product/system shall be applied in 2 or 3 coats as required , with a min total consumption of 6 kg/m2 to achieve a total thickness of Min 3mm., all as per manufacturers recommendations , etc complete. The product conforms to Min compressive strength > 30 Map at 28 days ageing, Adhesion to concrete surfaces shall be min 2 N/mm2 as per EN 1504-3, and Reaction to fire as per EN 13501-1( Euro class) conforming to A1.
| WTP External wall | Sqm
Sub Total
Total

## Service line & external sewage
PROJECT :NLSIU, BENGALURU
WATER DISTIBUITION SYSTEM TO BUILDINGS
Sl No | DESCRIPTION | UNIT | Nos | L | B | D | QTY | RATE
1 | SURVEYING WORKS
| Survey Total Station with surveyor | Days
Centreline marking
Plot survey after excavation
Floor finish RL marking
| Survey Auto level with surveyor | Days
1 | Trench works for service lines - L 1500 mts with CAST IN SITU- OPTION -01
| Excavation | Cum
| Backfilling | Cum
| Plain Cement concrete M10 | Cum
| RCC concrete- M25 Base | Cum
| wall concrete - M25 | Cum
| Top slab - In Size of 0.85 X 0.60 *0.11 | Cum
| Top slab - In Size of 0.85 X 0.60 *0.20 | Cum
| Shuttering works External | Sqm
| Internal | Sqm
| Top cover slab | Sqm
Reinforcement
1A | Trench works for service lines - L 1500 mts with Precast OPTION 02
| Excavation | Cum
| Backfilling | Cum
| Plain Cement concrete M10 | Cum
Supplying providing and installation of Pre cast U drain and cover slab unloading and laying and as directed by Engineer In charge.
| U Drain Normal Duty 2000 x 600 x 1000 with thickness of 100 mm | Rmt
Cover slab Normal duty- 1000 x 800 X 75mm thick
U Drain 2000 x 600 x 1000 with thickness of 150 mm
Cover slab Heavy duty- 1000 x 800 X 150mm thick
2 | RAIN WATER HARVESTING PIT IN STORM WATER TRENCH. Min 1.2 mt dia and 3.3 mt Depth with 250 mm Concrete rings OPTION 01
| Excavation | Cum
| volume of pit | Cum
| Back filling | Cum
| Concrete Rings of 1.2 mt dia | Nos
2A | RAIN WATER HARVESTING PIT IN STORM WATER TRENCH. Min 1.2 mt dia and 3.3 mt Depth with 250 mm Concrete rings with filter media- OPTION 02
| Excavation | Cum
| volume of pit | Cum
| Back filling | Cum
| Concrete Rings of 1.2 mt dia | Nos
| 1.5 mts Boulders 300 to 400 mm | Cum
| 600 mm stones 150 to 200 mm | Cum
| 450 mm pebbles 30 to 40 mm | Cum
| 300 mm coarse Sand | Cum
| COVER for 1.0 mt dia | L/s
2B | RAIN WATER HARVESTING PIT IN STORM WATER TRENCH. Min 1.2 mt dia and 3.3 mt Depth with precast elements - Option 03
| Excavation | Cum
| volume of pit | Cum
| Back filling | Cum
| Supplying, and installing of precast Rain water harvesting pits using for min depth of 3,0 mts including risers cover slab of internal diameter of 1200 mm etc., complete and as directed but Engineer in charge. . | Nos
Precast RCC RWH pit of 1200 mm Dia , for 3.0 mts Ht
Precast RCC RWH pit of 1500 mm Dia , for 3.0 mts Ht
3 | BORE WELL RECHARGE PITS- Min 3.0 Dia and 3.3 mts depth
| Excavation | Cum
| 1.5 mts Boulders of 300 to 400 mm | Cum
| 600 mm stones of 150 to 200 mm | Cum
| 450 mm pebbles of 30 to 40 mm | Cum
| HDPE mesh | Sqm
| 300 mm coarse Sand | Cum
| Slotted holes creating in MS casing pipe for 1.5 mts depth | L/s
4A | EXTERNAL SEWAGE SYSTEM. Length 1350 USING BBM- OPTION 01
| Excavation | Cum
| Excavation for chambers | Cum
| Plain cement concrete M10 Pcc 1:3:6 | Cum
| Backfilling | Cum
| RCC Hume Pipe 300 dia | Rmt
| Machine hole chambers of 1.2 mts internal dia with wire cut brick including plastering for both internal and on external surfaces. | No/ L/s
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth up to 1.2 and SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from to 1.5 to 2.0 mts and SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from 2.0 to 3.0 mt depth with SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from 3.0 to 4.0 mt depth with SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from 4.0 to 4.5 mt depth with SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from 4.5 to 5.0 mt depth with SFRC cover and frame.
Construction of Brick Masonry circular machine hole 1.2 internal dia for depth from 5.0 mt to 6.0 depth with SFRC cover and frame.
3A | EXTERNAL SEWAGE SYSTEM. Length 1350 USING PRECAST -OPTION 02
| Excavation | Cum
| Excavation for chambers | Cum
| Plain cement concrete M10 Pcc 1:3:6 | Cum
| Backfilling | Cum
| RCC Hume Pipe 300 dia | Rmt
Supplying and installing of RCC precast manhole for sewage manholes of internal dia 1200/1500
| Manhole 1200mm dia 125 thick for 1.2 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 1.5 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 2.0 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 2.5 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 3.0 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 3.5 mt Ht | Nos
| Manhole 1200mm dia 125 thick for 4.0 mt Ht | Nos
4 | WATER SUPPLY AND FLUSHING USING HDPE PIPES
| Excavation for Flushing and domestic lines | CUM
| HDPE for Flushing and domestic lines 90mm (OD) | Rmt
| Back filling | Cum
| Chambers 1000 X 1000 X 1000 | Nos
| Chamber 600 X 600X 1000 | Nos
5 | BORE WELL to WTP - HDPE PIPE 90 MM OD for 750 mts length
| Survey with Total station | Nos
| Excavation | Cum
| Back filling | Cum
| Inspection chambers RCC @ 30 mts intervals of 900 X 900 X 1000 mm | Nos
Inspection chambers RCC @ 30 mts intervals of 600 X 600 X 1000 mm
| Signage Boards | Nos
| HDPE 90 mm OD pipe | Rmt
| HDPE 90 mm OD pipe with collar | Nos
| Reinforcement for RCC chambers | Kgs
| Form work For RCC chambers | Sqm
| PCC for RCC chambers | Cum
| PLUM concrete | Cum